## Slide 1: iOPS for Salalah (SLL) airport

## Slide 2
10:30AM
2/29 SUN
63°F
85% RH
Login
SCREEN
6 CRITAL ALARMS
AVG Hook-up
3:45
-
-
-
-
User Name
Password
Reset User Name / Password
This time must come from central clock.
Auto Logout if not active for 15 min
User Level's: 1.) Normal Operator (Viewing Only) 2.) Maintenance (Viewing and reset service counters and service alarms) Level 3. Maintenance (Calibration and Configuration of Adjustable Parameters) Level 4 Administrator (Viewing and Controlling)

## Slide 3
10:30AM
2/29 SUN
63°F
85% RH
Salalah
SCREEN
Chart: OPERATIONS
| 1st Qtr | 2nd Qtr | 3rd Qtr | 4th Qtr
Sales | 8.2 | 3.2 | 1.4 | 1.2
Chart: PERFORMANCE
| Category 1 | Category 2
Series 1 | 4.3 | 2.5
Series 2 | 2.4 | 4.4
Series 3 | 2 | 2
6 CRITAL ALARMS
AVG Hook-up
3:45
-
-
-
-
Need to Replace Image
Not Ready = Error
Ready = No Alarms and has Power
Manual Operation = Bridge in Operate Mode.
Semi-Automatic Mode = Auto Level On
Error = Any Fault
Fire Alarm
23B
23F
25B
25F
29B
29F
31B
31F

## Slide 4
10:30AM
2/29 SUN
63°F
85% RH
Gate 1
SCREEN
Chart: OPERATIONS
| 1st Qtr | 2nd Qtr | 3rd Qtr | 4th Qtr
Sales | 8.2 | 3.2 | 1.4 | 1.2
Chart: PERFORMANCE
| Category 1 | Category 2
Series 1 | 4.3 | 2.5
Series 2 | 2.4 | 4.4
Series 3 | 2 | 2
6 CRITAL ALARMS
AVG Hook-up
3:45
-
-
-
-
Gate 2
Gate 3
Gate 4

## Slide 5
10:30AM
2/29 SUN
63°F
85% RH
Gate 1
SCREEN
Chart: OPERATIONS
| 1st Qtr | 2nd Qtr | 3rd Qtr | 4th Qtr
Sales | 8.2 | 3.2 | 1.4 | 1.2
Chart: PERFORMANCE
| Category 1 | Category 2
Series 1 | 4.3 | 2.5
Series 2 | 2.4 | 4.4
Series 3 | 2 | 2
6 CRITAL ALARMS
AVG Hook-up
3:45
-
-
-
-
Point |  |  | 
Remote Bridge Control |  |  | 
Operation Mode |  |  | 
E-Stop |  |  | 
AutoLevel |  |  | 
AutoLevel (Backup) |  |  | 
Canopy |  |  | 
Vertical Movement |  |  | 
… Up / Down / Limit |  |  | 
… Position | 15’ 5”/4.1 M |  | 
… Upper Limit | 28’ 5”/8 M |  | 
… Lower Limit | 8’ 5”/2.7M |  | 
Horizontal Movement |  |  | 
… Position (X/Y) | 15 / 54 |  | 
… Speed | 1.2 MPH |  | 
Tunnel Length (Feet / Metters) | 118 Ft / ?? M |  | 
Front Shutter / Doors |  |  | 
Sensor/Photo Cell |  |  | 
Encoders | 2341256 |  | 
PBB CCTV |  |  | 
Roof Top AC Units |  |  | 
Semi-Auto
Point |  |  | 
Power To Bridge |  |  | 
UPS Power Supply |  |  | 
Bridge Lighting |  |  | 
Emergency Lighting Power |  |  | 
Fire Alarm System |  |  | 
VDGS Interlock |  |  | 
PCA Pit |  |  | 
400hz Pit |  |  | 
Aircraft Type: | 747-400 |  | 
Aircraft Position: | ?????? |  | 
Dock Time | 14:35 |  | 
Un-Dock Time | 16:50 |  | 
ON
Off
Alarm
ON
ON
Off
Closed
Off
Not Ready
Ready
Man-Op
Not Ready
Ready / OK
Move-Up
Move-Dn
Up - Limit
Low - Limit
Forward
Backwards
Not Ready
Ready / OK
Open
Note: Show AC at Gate when in Semi-Auto Mode
Activated
Disabled
Ready / OK
Ready / OK
Extended
Retracted
Ready / OK
AutoLevel
Alarm
Ready / OK
Alarm
Clear
Occupied
Open
Closed
Open
Off
Alarm
Ready / OK
Activated
Operational
Alarm
Ready / OK
On
Note: When In AutoLevel Show AC at Gate
Note: Remote Control (On / Off)
Note: Remote Control (On / Off)

## Slide 6
10:30AM
2/29 SUN
63°F
85% RH
Gate 1 (Service Counters)
SCREEN
Chart: OPERATIONS
| 1st Qtr | 2nd Qtr | 3rd Qtr | 4th Qtr
Sales | 8.2 | 3.2 | 1.4 | 1.2
Chart: PERFORMANCE
| Category 1 | Category 2
Series 1 | 4.3 | 2.5
Series 2 | 2.4 | 4.4
Series 3 | 2 | 2
6 CRITAL ALARMS
AVG Hook-up
3:45
-
-
-
-
Point | Count | Reset Date | 
E-Stop (Count) | 345 | 06/01/14 | 
AutoLevel (Count) | 345 | 06/01/14 | 
AutoLevel (Backup) (Count) | 345 | 06/01/14 | 
Canopy (Count) | 345 | 06/01/14 | 
Vertical Movement (Count) | 345 | 06/01/14 | 
Horizontal Movement (Count) | 345 | 06/01/14 | 
Front Shutter / Doors (Count) | 345 | 06/01/14 | 
Sensor/Photo Cell (Count) | 345 | 06/01/14 | 
Roof Top AC Units (Count) | 345 | 06/01/14 | 
Power To Bridge (Count) | 345 | 06/01/14 | 
UPS Power Supply (Count) | 345 | 06/01/14 | 
Bridge Lighting (Count) | 345 | 06/01/14 | 
Fire Alarm System (Count) | 345 | 06/01/14 | 
VDGS Interlock (Count) | 345 | 06/01/14 | 
PCA Pit (Count) | 345 | 06/01/14 | 
400hz Pit (Count) | 345 | 06/01/14 | 
Note: Show AC at Gate when in Semi-Auto Mode
Reset All
Reset
Reset
Reset
Reset
Reset
Reset
Reset
Reset
Reset
Reset
Reset
Reset
Reset
Reset
Reset
Reset
Activated
Disabled
Remote Enable and Disable

## Slide 7
10:30AM
2/29 SUN
63°F
85% RH
Active Alarms Page
SCREEN
Chart: OPERATIONS
| 1st Qtr | 2nd Qtr | 3rd Qtr | 4th Qtr
Sales | 8.2 | 3.2 | 1.4 | 1.2
Chart: PERFORMANCE
| Category 1 | Category 2
Series 1 | 4.3 | 2.5
Series 2 | 2.4 | 4.4
Series 3 | 2 | 2
6 CRITAL ALARMS
AVG Hook-up
3:45
-
-
-
-
Page for Alarms and Alarm Summary's: All alarms shall have alarm counters that are resettable for the operator. All Alarms shall be saved for a minimum of one year. Alarms shall be divided into separated groups. It Shall be possible to acknowledge an alarm in the alarm list and jump directly to the page containing the part triggering the alarm

## Slide 8
10:30AM
2/29 SUN
63°F
85% RH
Network Monitoring
SCREEN
Chart: OPERATIONS
| 1st Qtr | 2nd Qtr | 3rd Qtr | 4th Qtr
Sales | 8.2 | 3.2 | 1.4 | 1.2
Chart: PERFORMANCE
| Category 1 | Category 2
Series 1 | 4.3 | 2.5
Series 2 | 2.4 | 4.4
Series 3 | 2 | 2
6 CRITAL ALARMS
AVG Hook-up
3:45
-
-
-
-
Server A
Server B
SCADA Redundancy (Switch from one scada to the other from the HMI and to be able to see which one is active.

## Slide 9
10:30AM
2/29 SUN
63°F
85% RH
Flight Data-Inbound
SCREEN
Chart: OPERATIONS
| 1st Qtr | 2nd Qtr | 3rd Qtr | 4th Qtr
Sales | 8.2 | 3.2 | 1.4 | 1.2
Chart: PERFORMANCE
| Category 1 | Category 2
Series 1 | 4.3 | 2.5
Series 2 | 2.4 | 4.4
Series 3 | 2 | 2
6 CRITAL ALARMS
AVG Hook-up
3:45
-
-
-
-
Flight Data-Outbound
SCADA Shall Display (Aircraft Type and Model, Aircraft Position, Docking time, Undocking Time, Information from the 400hz Power Supply System Regarding Pits / Hatches, On Block and Off Block)

## Slide 10
10:30AM
2/29 SUN
63°F
85% RH
Flight Data-Inbound
SCREEN
Chart: OPERATIONS
| 1st Qtr | 2nd Qtr | 3rd Qtr | 4th Qtr
Sales | 8.2 | 3.2 | 1.4 | 1.2
Chart: PERFORMANCE
| Category 1 | Category 2
Series 1 | 4.3 | 2.5
Series 2 | 2.4 | 4.4
Series 3 | 2 | 2
6 CRITAL ALARMS
AVG Hook-up
3:45
-
-
-
-
Flight Data-Outbound
Today
Drop-Down to select Today, yesterday, last week, last month. Year, year to day. Install Date to To-Day
Charts:
Gate utilization
Alarms by group
Alarms by gate
Number of cycles
Hours of operation
Current status
Top 4 alarms by group
Average gate turn times
Same for 400hz along with
Output voltage high and low
400hz high Avg

## Slide 11
10:30AM
2/29 SUN
63°F
85% RH
Reports
SCREEN
Chart: OPERATIONS
| 1st Qtr | 2nd Qtr | 3rd Qtr | 4th Qtr
Sales | 8.2 | 3.2 | 1.4 | 1.2
Chart: PERFORMANCE
| Category 1 | Category 2
Series 1 | 4.3 | 2.5
Series 2 | 2.4 | 4.4
Series 3 | 2 | 2
6 CRITAL ALARMS
AVG Hook-up
3:45
-
-
-
-
Gate
Today
Start Date/Time
Aircraft
Aircraft Type
End Date/Time
Point 1
Point Type
Point 2
Point 3
Point 4
Drop-Down to select Value, Just put data Into Grid with a way to export to Excel

## Slide 12
General Instructions
All Starting Manoeuvers shall be confirmed. Maneuvers shall be logged by time and user
Page for Setup : The following parameters shall be able to be set as a minimum All changeable Parameters for each PBB / User Access Rights
Page for Trends shall be fully configurable in time/ Value / Number of curves and printable
Tool Tips: Tool Tips shall contain the physical name when placing the mouse over the object. It shall be possible to activate, de activate the tool tip function
Screen Resolution: 1024 x 768 and 32 bit as a minimum
Reports: It shall be fully configurable for the operator to select which information shall be in the report
Report Editing Tool shall be included
SCADA system to transfer critical alarms and status information through the AODB to the airport SCAD system. According to the project specified XML scheme. Participation in testing of the Airport Scada Interface to the Bridge
Remote Control of AC
Remote Control of Lights
Notes:
How will the VDGS - PBB Defect and Error Handling be recorded.

## Slide 13
Network Configuration
  SLL
    PBB Server 01 (SLL_DC1_MCS_SERV01) I.P. 10.181.246.200/24 DNS (10.181.246.30/24)
    PBB Server 02 (SLL_DC2_MCS_SERV02) I.P. 10.181.246.201/24 DNS (10.181.246.30/24)
    PBB Workstation 01
    PBB Workstation 02
  MCT Phase 2
    PBB Server 01 (MCT_DC2_MCS_SERV01) I.P. 10.238.246.200/24 DNS (10.238.246.30/24)
    PBB Server 02 (MCT_DC2_MCS_SERV02) I.P. 10.238.246.201/24 DNS (10.238.246.31/24)
    PBB Workstation 01
    PBB Workstation 02
BH-04 | 23F (IN Board) | PLC | 10.174.20.1
 |  | HMI | 10.174.20.2
 |  | CCTV | 10.174.20.3
 |  | PHONE | 10.174.20.4
 |  | CARD | 10.174.20.5
BH-04 | 23B (OUT Board) | PLC | 10.174.20.6
 |  | HMI | 10.174.20.7
 |  | CCTV | 10.174.20.8
 |  | PHONE | 10.174.20.9
 |  | CARD | 10.174.20.10
BH-03 | 25F (IN Board) | PLC | 10.174.20.11
 |  | HMI | 10.174.20.12
 |  | CCTV | 10.174.20.13
 |  | PHONE | 10.174.20.14
 |  | CARD | 10.174.20.15
BH-03 | 25B (OUT Board) | PLC | 10.174.20.16
 |  | HMI | 10.174.20.17
 |  | CCTV | 10.174.20.18
 |  | PHONE | 10.174.20.19
 |  | CARD | 10.174.20.20
BH-02 | 29F (IN Board) | PLC | 10.174.20.21
 |  | HMI | 10.174.20.22
 |  | CCTV | 10.174.20.23
 |  | PHONE | 10.174.20.24
 |  | CARD | 10.174.20.25
BH-02 | 29B (OUT Board) | PLC | 10.174.20.26
 |  | HMI | 10.174.20.27
 |  | CCTV | 10.174.20.28
 |  | PHONE | 10.174.20.29
 |  | CARD | 10.174.20.30
BH-01 | 31F (IN Board) | PLC | 10.174.20.31
 |  | HMI | 10.174.20.32
 |  | CCTV | 10.174.20.33
 |  | PHONE | 10.174.20.34
 |  | CARD | 10.174.20.35
BH-01 | 31B (OUT Board) | PLC | 10.174.20.36
 |  | HMI | 10.174.20.37
 |  | CCTV | 10.174.20.38
 |  | PHONE | 10.174.20.39
 |  | CARD | 10.174.20.40
Servers |  | Server -1 | 10.174.20.41
 |  | Server -2 | 10.174.20.42
Work Stations |  | Work station -1 | 10.174.20.43
 |  | Work station -2 | 10.174.20.44

## Slide 14
Screen background (rgb 255, 255, 246)
Structure/Terminal Color (rgb 80, 80, 60) 30% transparency
Menu icon (rgb 255, 216, 76)
Title, Gate Numbers, Highlighted Menus (rgb 43, 43, 43)
Non- Highlighted Menus (rgb 201, 201, 187)
Alert (rgb 192, 80, 77)
Graph / Box Outline color (rgb 191, 191, 191) size 0.25 pt
Second header bar/box header (rgb 80, 80, 60) 0% transparency
Side menu bar (rgb 191, 191, 191) size 1.25 pt
Arial Font